	HYDROSTATIC PRESSURE TEST & LEAKAGE TEST REPORT
EXTERNAL PIPELINE 
	Form QT4(a)

	
	Page 1 of 2


	Name of Development
	:
	

	
	
	

	
	
	

	   
	
	

	
	
	

	Project Reference No.
	:
	


1. Pressure Test
	Testing Date
	:
	
	Time :
	

	Preperations for Test
	:
	Satisfactory / Not Satisfactory


	Description Of Pipeline
	Max Lenght
	(√)
	
	Pipe Material
	Pressure Test (Bar)
	(iii)
Leakage Test (Bar)

	Trunk Main
	3 km
	
	
	HDPE (PN12.5)
	12.0
	8.0

	Reticulation Pipe
	2km
	
	
	Steel
	15.0
	12.0

	
	
	
	
	Ductile Iron
	15.0
	12.0

	
	
	
	
	ABS (CL 12)
	12.0
	8.0


	Pipe Material
	Pipe Location
	(i)

Internal Pipe Dia.

(mm)-
	(ii)

Pipe Lenght

(m)
	Initial Specified Pressure (Bar)
	Final Pressure after 10mins / 1 hour (Bar)*
	Result

	
	From; 

Pt./ CH./ Node
	To; 
Pt./ CH./ Node
	
	
	
	
	Pass √
	Fail X

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	


* Steel Pipe : The pressure must stand at 15 Bar for 10 minutes with no allowable drop.
* HDPE Pipe : The pressure must stand at 12 Bar for 1 hour with the allowable drop of 0.1bar (max).
2. Leakage Test – External Pipeline & Main Pipe
	Testing Date
	:
	
	Time :
	

	Preperations for Test
	:
	Satisfactory / Not Satisfactory


	
	
	
	
	
	

	
	(i)
	(ii)
	
	(iii)
	

	Allowable Leakage For Steel Pipe
	=
	0.34 liter x    
	internal pipe dia. (mm) x 
	pipe length (m) x 
	total test duration (hour)  x 
	leakage test (bar) 
	(Liters)

	
	
	10 x 1000 x 24 hr x 1 bar
	


	Pipe Location
	(iv) Allowable Leakage*
	Initial 

Specified Pressure

(Bar )
	Final Pressure

(Bar)
	Total make-up water

(liter)
	Result

	From; 

Pt./ CH./ Node
	To; 

Pt./ CH./ Node
	
	
	
	
	Pass √
	Fail X

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


* Steel Pipe : The pressure must stand at 12 Bar for 24 hrs with the alowable drop within the specified rate 
 * HDPE Pipe : The pressure must stand at 8 Bar for 2 hrs with no allowable drop 
	HYDROSTATIC PRESSURE TEST & LEAKAGE TEST REPORT

EXTERNAL PIPELINE 
	Form QT4(a)

	
	Page 2 of 2


Note: The pressure chart recorder result shall be attached with this report.
	Checked By  


	
	

	Name 

	:
	

	Firm

CP Registration No        
	:

:
	

	NRIC. No.
	:
	

	 Date                           :
	Signature of Competent Person



	Witnessed By  


	
	

	Name 

	:
	

	Staff No
	:
	

	
	Signature of AIR SELANGOR; 

Executives/ Technician

Regional Development Unit


Date                           :

PAGE  

